## Requirements
The Tenderer agrees the answers in this response template have a higher contractual priority as additional delivered information by the Tenderer.
The Tenderer will indicate in the column "Deployed TSO reference(s)" in which TSO the functiionality is already deployed and in real operation.
ID | Category | Requirement | Demo | Minimal Requirement | Answer | Deployed TSO reference(s) | Short description of the solution
| Basic requirements | The offered solution is capable to handle at least 250 PMU's simultaneously with the information flow defined under the requirements below |  | Yes
| Basic requirements | The offered solution is capable to handle at least 10 lower level PDC's simultaneously (client & server functionality, on top of all PMU's) with the information flow defined under the requirements below |  | No
| Basic requirements | The offered solution will be capable to handle PMU's (or PMU's connected to the lower-level PDC's) with a reporting rate up to 50 fps |  | Yes
| Basic requirements | The offered solution will be capable to handle PMU's (or PMU's connected to the lower-level PDC's) with a reporting rate up to 100 fps |  | No
| Basic requirements | The offered solution will be capable to handle PMU's (or PMU's connected to the lower-level PDC's) with a reporting rate up to 200 fps. |  | No
| Basic requirements | The offered solution will be capable to handle min 8 phasors per PMU (or per PMU connected to the lower level PDC) |  | Yes
| Basic requirements | The offered solution will be capable to handle min 16 phasors per PMU (or per PMU connected to the lower level PDC) |  | No
| Basic requirements | The offered solution will be able to collect both three phase measurement (components) data (frequency, phase angle, magnitude) and positive sequence data. |  | Yes
| Basic requirements | The offered solution will be capable to handle large network latency up latency as defined in the "interfacing requirement" document. As a result, "waiting time" for time alignment between all data is required. This "waiting time" will be configurable. |  | Yes
| Basic requirements | It will be possible with the offered solution to define alerts and loggings, e.g. - alarms - incoming data not valid - WAMS functionality not working correctly - trigger on all measurements or specific logic for output configuration |  | Yes
| Basic requirements | The offered solution will detect components of the offered solution are not running anymore (e.g. data acquisition, functional components like Power Osciillation monitoring component, Power Oscillation Locator component, ...). The non correct behavior of some components of the solution will be visualized in the solution. |  | Yes
| Basic requirements | The non correct behavior of some components of the solution can be communicated to the SCADA/EMS system via IEC 60870-5-104 |  | No
| Basic requirements | The non correct behavior of some components of the solution can be communicated to an external monitoring system (e.g.Elia internal monitoring system, E-mail, …) via the interfaces as requested in the "interfacing requirement" document. |  | No
| Basic requirements | The tenderer will provide a proposed complete architectural overview of the offered solution. The architectural overview will contain all components required for the solution. The architectural overview will explain all data flows for all requirements between the different components. The architectural overview will explain the choices made to meet the requirements (e.g. security, performance, ... e.g. flows real-time data, flows historical data, ...). |  | Yes
| Basic requirements | During project phase, the supplier will supply technical documentation of the solution: - technical description of the solution and the HW/SW architecture - functional description of the solution - manuals - IT installation requirements, IT installation manuals/procedures, IT automatic backup procedures, ... - ... |  | Yes
| Data Validation | The offered solution will perform data validation check by the PDC on all incoming data (from PMU's or other PDC's), e.g. |  | Yes
|  | - checking data status flags and time quality |  | No
|  | - invalid or corrupted data |  | No
|  | - data integrity checks |  | No
|  | - data authentication checks |  | No
|  | - PMU in service |  | No
|  | - PMU out of service |  | No
|  | - communication anomaly |  | No
|  | - missing data |  | No
|  | - data in the future |  | No
|  | - data out of range |  | No
|  | - not synchronized data |  | No
|  | - duplicated data |  | No
|  | - … |  | No
| Data Validation | The tenderer will indicate which data validation checks and checks functionalities are available in the offered solution |  | Yes
| Data Validation | Any incoming data not passing all validation checks will be logged by the offered solution and the output data stream will be flagged accordingly to the type of erroneous data. |  | Yes
| Data Validation | Any incoming data not passing all validation checks will generate an alarm by the offered solution. |  | Yes
| Data Validation | Any incoming data not passing all validation checks generating an alarm can be forwarded to the SCADA/EMS system via IEC 60870-5-104 |  | No
| Data Validation | Any incoming data not passing all validation checks generating an alarm can be forwarded to an external monitoring system (e.g. Elia internal monitoring system, E-mail, …) via the interfaces as requested in the "interfacing requirement" document. |  | No
| Data acquisition and forwarding | The Tenderer will describe fully the performance of the "data acquisition and forwarding" module. |  | Yes
| Data acquisition and forwarding | The offered solution (PDC) shall include data quality, time quality and time synchronziation for each signal into the output data frame |  | No
| Data acquisition and forwarding | The offered solution can synchronize to absolute time (an absolute time is UTC time) |  | Yes
| Data acquisition and forwarding | The offered solution can synchronize to relative time (a relative time is an event, an event may be the arrival of the first data with a specific timestamp) |  | No
| Data acquisition and forwarding | The offered solution can handle different data streams: |  | Yes
|  | - different contents (e.g. on top of the 8 standard syncrhophasors, on top e.g. an analogue signal, …) |  | Yes
|  | - different rate (fps) (e.g. samples with 10 fps, others with 20 fps, …) |  | Yes
|  | - different waiting times |  | No
| Data acquisition and forwarding | The offered solution is able to sent data streams to different locations and devices (internal or external to ELIA), e.g. |  | Yes
|  | - Elia's SCADA system |  | Yes
|  | - external PDC, EAS system |  | Yes
|  | - external PDC, other TSO's |  | Yes
|  | - other offline analysis tools |  | No
| Data acquisition and forwarding | The offered solution can handle data forwarding (e.g. to PDC of other TSO, EAS system, …): |  | No
|  | - with modification of the content |  | No
|  | - without modification of the content |  | No
|  | - single input stream to single input stream |  | No
|  | - single input stream to single output stream |  | No
|  | - single input stream to multiple output streams |  | No
|  | - a single PMU stream (or a selected list of PMU streams) to the PDC (EAS, other TSO's) |  | Yes
| Data acquisition and forwarding | The offered solution will be UTC synchronized |  | Yes
| Data acquisition and forwarding | The offered solution will perform data latency evaluation |  | Yes
| Data acquisition and forwarding | The offered solution will be able to give statistics and store the data latency in the database |  | No
| Data acquisition and forwarding | The offered solution will be able to process the incoming C37.118 data in real time and perform time alignment based on PMU time stamp |  | Yes
| Data acquisition and forwarding | During the processing of incoming data, the offered solution will evaluate the status of operation for - each input/output - communication quality - processing and alignment of time - data latency |  | No
| Data acquisition and forwarding | The offered solution will log issues occuring during the processing of incoming data. |  | Yes
| Data acquisition and forwarding | The offered solution will log issues occuring during the processing of incoming data. The offered solution will be able to sent alarms about the status of operation of external systems to the SCADA/EMS system via IEC 60870-5-104 |  | No
| Data acquisition and forwarding | The offered solution will log issues occuring during the processing of incoming data. The offered solution will be able to sent alarms about the status of operation of external systems via the interfaces as requested in the "interfacing requirement" document. |  | No
| Conversion and Manipulation | The offered solution (PDC) will be able to convert data with different reporting rates (fps) - from all the input to all the output data streams specified in IEEE C37.118.1-2011 |  | Yes
| Conversion and Manipulation | The offered solution will be able to collect data of different reporting rates |  | Yes
| Conversion and Manipulation | The offered solution will be able to send data to different applications at different rates at the same time |  | Yes
| Conversion and Manipulation | The offered solution will be able to configure a different reporting rate for each input and output data stream by the user |  | No
| Conversion and Manipulation | The offered solution will be able to apply up-down conversion |  | No
| Conversion and Manipulation | The offered solution will be able to indicate data is missing or incomplete. |  | Yes
| Conversion and Manipulation | The offered solution will be able to substitue (automatically) wrong data in the stream (missing, invalid, corrupted, …) |  | No
| Conversion and Manipulation | The offered solution will guarantee the result of the data manipulations is always IEEE compliant |  | Yes
| Conversion and Manipulation | The offered solution shall apply linear manipulation/simple math to the data stream (summing currents from different PMU streams for example) to create new observable/data streams |  | Yes
| Conversion and Manipulation | The offered solution shall apply simple manipulations to the input data (e.g. inverting angles, converting coordinates, convert fixed-floating point, converting to sequence data) |  | Yes
| Conversion and Manipulation | The offered solution can receive data in rectangular or polar angle form and fixed or floating point and can convert data from-to each of these formats |  | No
| Data storing | The offered solution will be able to store synchrophasor data - raw data and adapted data (e.g. linear manipulation, polar/rectangular, floating/fixed point, …) with the data validation flags and data latency information |  | Yes
| Data storing | Reporting rate in the database shall be selectable and different reporting rate storage shall be possible for different synchrophasors |  | No
| Data storing | The offered solution will be able to store the results of the WAMS system calculations: - the results of the functional evaluations /algorithm/processes - the alarms triggered |  | Yes
| Functional Requirements | The offered solution shall include a Real time Power Oscillation Monitoring and detection system | DEMO 5 | Yes
| Functional Requirements | The offered solution shall have a functionality to output the amplitudes of the detected oscillations | DEMO 5 | Yes
| Functional Requirements | The offered solution shall have a functionality to output the frequencies of the detected oscillations | DEMO 5 | Yes
| Functional Requirements | The offered solution shall have a functionality to output the damping coefficients of the detected oscillations | DEMO 5 | Yes
| Functional Requirements | The offered solution shall have a functionality to output the energies of the detected oscillations | DEMO 5 | No
| Functional Requirements | The offered solution shall have a functionality to output the participation factors of the detected oscillations | DEMO 5 | Yes
| Functional Requirements | The range of frequency to be observed by the realtime power oscillation monitoring shall be between 0 Hz and the Nyquist frequency of the signal (0.5 * max fps (min 50 fps) – [0Hz – 25Hz]) | DEMO 5 | Yes
| Functional Requirements | The range of frequency to be observed by the realtime power oscillation monitoring shall be between 0 Hz and the Nyquist frequency of the signal with more than 50 fps | DEMO 5 | No
| Functional Requirements | The offered solution shall use as input for the power oscillation monitoring any of the synchrophasor data (Voltage Magnitude, Voltage Angle, Current Magnitude, Current Angle, Active Power, Reactive Power, Frequency, ROCOF…) | DEMO 5 | Yes
| Functional Requirements | The offered solution shall include a Real Time Power Oscillation Locator | DEMO 6 | Yes
| Functional Requirements | The Real Time Power Oscillation Monitoring and Locator shall provide a ranking of the synchrophasor or composed input that impact the most the different oscillation modes | DEMO 6 | Yes
| Functional Requirements | The ranking of the Real Time Power Oscillation Monitoring and Locator shall be performed based on the input synchrophasor or composed input data and per oscillation mode detected | DEMO 6 | Yes
| Functional Requirements | The proposed power oscillation monitoring function and Real Time Power Oscillation Locator are able to detect ring-down event oscillations |  | Yes
| Functional Requirements | The proposed power oscillation monitoring function and Real Time Power Oscillation Locator are able to detect background oscillations and forced oscillation events | DEMO 7 | Yes
| Functional Requirements | The functionalities of Realtime Power Oscillation Monitoring and Power Oscillation Locator shall use as input separate PMU streams (Single PMUs synchrophasors) |  | Yes
| Functional Requirements | The functionalities of Realtime Power Oscillation Monitoring and Power Oscillation Locator shall use as input a combination of PMU streams (e.g. group of PMUs Synchrophasors) |  | Yes
| Functional Requirements | The functionalities of Realtime Power Oscillation Monitoring and Power Oscillation Locator shall use as input a composed set input data = mathematical combination of synchrophasor data (e.g. the sum of active power of different synchrophasors) | DEMO 5/DEMO6 | Yes
| Functional Requirements | The offered solution for Realtime Power Oscillation Monitoring and Power Oscillation Locator shall be able to use several inputs (to be clarified how much by the Tenderer) per oscillation monitoring and several inputs (to be clarified how much by the Tenderer) for locator instance. Multiple instances shall also be possible. | DEMO 5 | Yes
| Functional Requirements | The offered solution for Realtime Power Oscillation Monitoring and Power Oscillation Locator shall be able to use at least 30 inputs per oscillation monitoring and 30 inputs for locator instance. Multiple instances shall also be possible. |  | No
| Functional Requirements | The offered solution shall include a realtime ROCoF calculation functionality |  | Yes
| Functional Requirements | The ROCoF calculation functionality can give the user the capability to define the observation interval of the ROCoF estimation |  | No
| Functional Requirements | The offered solution shall generate "ROCoF-based alarming". An alarm shall be triggered in real-time when the ROCof is above or below a specific threshold value for more than a specific amount of time |  | Yes
| Functional Requirements | The offered solution can include a realtime voltage angle difference calculation |  | No
| Functional Requirements | The realtime voltage angle difference functionality calculates and show on a map the voltage angle difference between several PMUs |  | No
| Functional Requirements | The realtime voltage angle difference functionality calculates and show on a Single Line Diagram the voltage angle difference between several PMUs |  | No
| Functional Requirements | The offered solution can generate "voltage angle alarming". An alarm can be triggered in real-time when the voltage angle is above or below a specific threshold value for more than a specific amount of time |  | No
| Functional Requirements | The offered solution can include a realtime islanding detection functionality |  | No
| Functional Requirements | the realtime islanding detection functionality calculates island networks and support the operators during blackstart / reconstruction |  | No
| Functional Requirements | The offered solution can be able to download, visualize and compare the waveforms coming from a measurement device in the field |  | No
| Functional Requirements | The offered solution can be able to analyse waveforms to detect oscillation modes in a similar way as the power oscillation monitoring functionality |  | No
| Functional Requirements | The offered solution for waveform analysis can be able to correlate oscillation coming from different waveform recorders to suggest the operator the sources of high frequency interaction |  | No
| Functional Requirements | The offered solution for waveform analysis can be able to use as input a composed set of input data= mathematical combination of waveform data (e.g. sum of current of different waveform measurement units) |  | No
| Functional Requirements | The solution proposed can be able to apply basic data mathematical analysis functions to the output of the available functionalities (i.e. Realtime Power Oscillation Monitoring, Power Oscillation Locator, ROCoF Calculation, Voltage phase difference calculation, Islanding detection) |  | No
| Functional Requirements | The offered solution shall have the possibility to define realtime alarm on any value of synchrophasor received, calculated values or combination of these (e.g. sum of power injected by different phasors) | DEMO5/DEMO6 | Yes
| Functional Requirements | The offered solution can have the possibility to define a realtime alarm on any variation (e.g. derivative d/dt) of value of synchrophasor or calculated values |  | No
| Functional Requirements | The offered solution shall have the possibility to define realtime alarm on any value of calculated output or post-processed value. This includes all the output of all the analysis algorithms (e.g. power oscillation monitoring, power oscillation locator,…) | DEMO3/DEMO5/DEMO6 | Yes
| Functional Requirements | The offered solution can have the possibility to define a realtime alarm on any variation of value (e.g. derivative d/dt) of calculated outputs or post-processed value. This includes all the output of the analysis algorithms (e.g. power oscillation monitoring, power oscillation locator,…) |  | No
| Functional Requirements | The thresholds for alarm activation shall contain an hysteresis |  | No
| Functional Requirements | The alarm activation signal shall be transferrable to an external entity (e.g. EMS system, EAS system, … ) according to response template interfacing requirements. | DEMO3/DEMO5/DEMO6 | Yes
| Functional Requirements | The offered solution will be able to handle and execute user defined algorithms. The tenderer will indicate which coding language (e.g. C, C++, …) are supported. The offered solution will compile the user defined algorithms. The user defined algorithms will be able to receive inputs like phasor data, internal variables, ... The tenderer will explain how the algorithms can be put into operation by the offered solution. |  | No
| Functional Requirements | The offered solution will offer the possibility to the end user to create vizualisation interfaces for user defined algorithms. |  | No
| Functional Requirements | With the offered solution it is possible to receive data from internal Elia of other 3th party applications and include them in calculations offered by the solution (e.g. mix PMU data with RTU data and performing calculations based on both data sources). |  | No
| Visualization | The offered solution will be able to visualize in real-time PMU data | DEMO 3 | Yes
| Visualization | The offered solution will be able to visualize in real-time the results of WAMS functionalities | DEMO 3 | Yes
| Visualization | The offered solution will be able to visualize historical data: | DEMO 2 | Yes
|  | - of all the PMU data including diagnostic data | DEMO 2 | Yes
|  | - of all the WAMS functionalities output, including diagnostic data and quality data | DEMO 2 | Yes
| Visualization | The offered solution will include an interface or tool/file to configure input data streams (including PDC wait time, alarm threshold levels, ...) |  | Yes
| Visualization | The offered solution will include visualization interface for performing monitoring and diagnostic for each of the input and output data streams |  | Yes
| Visualization | The offered solution will include an alarm presentation interface, this alarm presentation interface should have the possibility to lock it in a prominent place on the HMI. | DEMO 3 | Yes
| Visualization | The offered solution will include a visualization interface for the different functionalities, e.g. |  | Yes
|  | PMU parameters |  | Yes
|  | configuration frame management |  | No
|  | data and manipulation functions |  | Yes
|  | reporting rate conversion |  | Yes
|  | replacement of missing data |  | Yes
|  | … |  | No
|  | The configuration frame management of the offered solution is fully documented by the Tenderer |  | No
| Visualization | The offered solution will include a visualization interface for the configuration of data storage (storage time, variables, …) |  | No
| Visualization | The offered solution will include a visualization interface for monitoring data latency for each input stream and for the monitoring of performance |  | No
| Visualization | The offered solution will include a vizualization interface for monitoring the performance of individual compontents (e.g. PDC, …) of the offered solution. |  | No
| Visualization | The offered solution will include a visualization interface to select data to be exported, file format (Comtrade, TXT, CSV, …) and relative time range | DEMO 4 | Yes
| Visualization | The offered solution will include a visualization interface to select data to be exported: - a single PMU, mutiple PMU's, all PMU's, all data streams, … - select PMU values to be exported (e.g. voltage magnitudes, voltage phase angles, frequencies, …) - specific data selection (e.g. data exceeding a specific threshold for a specific amount of time during a specific time frame, all PMU data when the ROCOF was higher than a specific value for mor than a specific amount of time, ...) | DEMO 4 | Yes
| Visualization | The offered solution will include a visualization interface to monitor and diagnose the data saving function |  | No
| Visualization | The offered solution will include dedicated charts to display synchro phasors and results of WAMS analysis in real time and for historical data: | DEMO 2/DEMO3 | Yes
|  | - basic plot with time on the x axis | DEMO 2/DEMO3 | Yes
|  | - advanced plot with any of the synchrophasor as X and Y axis (e.g. P on the X and FREQ on the Y) | DEMO 2/DEMO3 | No
|  | - different synchrophasors from different PMUs in the same plot | DEMO 2/DEMO3 | Yes
|  | - Same graph, same synchrophasor from the same PMU in the same plot (e.g. different zoom lervel on different trends) | DEMO 2/DEMO3 | No
|  | - different synchrophasor data from the same PMU in the same plot (e.g. voltage angle, voltage magnitude) | DEMO 2/DEMO3 | Yes
|  | - zoom and tooltip | DEMO 2/DEMO3 | No
|  | - cursor and hoover function | DEMO 2/DEMO3 | No
|  | - axis scaling | DEMO 2/DEMO3 | Yes
| Visualization | The offered solution shall include dedicated charts to display synchro phasors and results of WAMS analysis in real time and for historical data: | DEMO2 | Yes
|  | - Topological view (SLD) | DEMO2 | Yes
|  | - geographical view with the possibility to show variables (measurements, results of analysis) on the gepgraphical representation with coloration based on value/alarm/result of WAMS analysis | DEMO2 | No
| Visualization | The offered solution will include a user interface for WAMS functionalities (each one separate), as for the input configuration parameters, as for the output results |  | Yes
| Visualization | The offered solution will include a user interface to visualize the status of the different PMU's (synthetic diagnostic visualization) |  | Yes
| Visualization | The offfered solution shall include trends time range to be visualized based on: |  | Yes
|  | - real time visualization | DEMO3 | Yes
|  | - pre-defined time range (e.g. 1 day, 1 week, …) | DEMO2 | No
|  | - choice based on calendar time/date | DEMO2 | Yes
| Visualization | It will be possible with the offered solution to filter/search the measurements or the results of the WAMS analysis via a specific functionality |  | No
| Visualization | With the offered solution, the trends and the user interface will be configurable by the user and stored into a profile based on the user that is currently logged on. A basic user interface will be put at disposal to all uers of the offered solution. | DEMO3 | No
| Visualization | The offered solution will be single sign on based (based on Windows log on credentials) | DEMO2 | No
| Visualization | The offered solution allows simultaneous connection of several users, only limited by the offered license model | DEMO2 | Yes
| Visualization | The complete user interface will be at least be in English. The Tenderer will indicated which other languagues are supported. | DEMO 2 | Yes
| PMU stream simulator | The offered solution will include a PMU stream simulator compatible with C37.118-2011 |  | No
| PMU stream simulator | The offered solution will include a PMU stream simulator compatible with IEC61850-9-5 |  | No
| PMU stream simulator | The offered solution will include a stream of lower level PDC simulator compatible with IEEEC37.244-2013 |  | No
| PMU stream simulator | The offered solution will include a stream of lower level PDC simulator compatible with IEEE C37.247-2019 (and/or the latest version) |  | No
| PMU stream simulator | The PMU simulator will be able to generate one or multiple streams of data based on: | DEMO 7 | Yes
|  | - measurement input from csv/txt file and/or COMTRADE file |  | Yes
|  | - past measurement information stored in the historian database |  | Yes
| PMU stream simulator | For the creation of the PMU streams, the simulator will be interfaceable with power system simulators: |  | No
|  | - RTDS |  | No
|  | - DigSilent - PowerFactory |  | No
|  | - PSCAD |  | No
|  | - … (the tenderer will indicate with which other systems the simulator is interfaceable) |  | No
| PMU stream simulator | With the offered solution, it will be possible to modify the data streams (e.g. delaying some of the PMU streams, setting quality bytes in the PMU frames, …) |  | No

## Value Definitions
Requirement Category | Minimal Requirement | Answer
Basic requirements | Yes | Yes, standard
Data acquisition and forwarding | No | No, not provided
Data Validation
Interfacing and protocols
Functional Requirements
Conversion and Manipulation
Data storing
Visualization
PMU stream simulator