## Requirements
The Tenderer agrees the answers in this response template have a higher contractual priority as additional delivered information by the Tenderer.
The Tenderer will indicate in the column "Deployed TSO reference(s)" in which TSO the functiionality is already deployed and in real operation.
ID | Category | Requirement | Demo | Minimal Requirement | Answer | Deployed TSO reference(s) | Short description of the proposal
| Standards | The offered solution will be capable to handle PMU of the supplier XXXX of type YYYY | DEMO 1 | Yes
| Standards | The offered solution will be capable to collect data from different PMU vendors and different types of PMUs |  | Yes
| Standards | The offered solution will be compliant with the latest version of C37.244 (at least C37. 244-2013) |  | Yes
| Standards | The offered solution will be compliant with the latest version of C37.247-2019 and/or the latest version. |  | No
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via C37.118.2-2011 standard. The offered solution will be fully compliant. | DEMO 1 | Yes
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via C37.118-2005 standard. The offered solution will be fully compliant. |  | No
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via a C37.118 via the ENTSO-E EAS system conform the requirements of all ENTSO-E EAS system. (EAS = European Awareness System") |  | Yes
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via IEC 61850-90-5 standard. The offered solution will be fully compliant. |  | No
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via IEC 61850-90-5 Ed2.1 standard. The offered solution will be fully compliant. |  | No
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via OPC-UA (e.g. directly coming from other TSO's, …) |  | No
| Standards | The offered solution will be capable to receive, parse and interpret data from PMU's and PDC's via OPC-UA via the ENTSO-E EAS system conform the requirements of all ENTSO-E EAS system. (EAS = European Awareness System") |  | No
| Standards | The offered solution will be capable to send data to other PDC's (e.g. to other TSO's) via C37.118.2-2011. The offered solution will be fully compliant. | DEMO 1 | Yes
| Standards | The offered solution will be capable to send data to the ENTSO-E EAS system via C37.118 conform all requirements of the ENTSO-E EAS system. (EAS = European Awareness System") |  | Yes
| Standards | The offered solution will be capable to send data to other PDC's via C37.118-2005. The offered solution will be fully compliant. |  | No
| Standards | The offered solution will be capable to send data to other PDC's via IEC 61850-90-5. The offered solution will be fully compliant. |  | No
| Standards | The offered solution will be capable to send data to other PDC's via IEC 61850-90-5 Ed2.1. The offered solution will be fully compliant. |  | No
| Standards | The offered solution will be capable to send data via OPC-UA |  | No
| Standards | The offered solution will be capable to send data to the ENTSO-E EAS system via OPC-UA conform all requirements of the ENTSO-E EAS system. (EAS = European Awareness System") |  | No
| Standards | The offered solution will be capable to support CFG frames (configuration frames) as defined in IEEE C37.118: - Receive configuration frames unsolicited from data source​ - Request configuration frames to the data source​ - Request configuration frame automatically or based on user request​ - Recognize a change in configuration for CFG-2 frames and takes necessary actions without interruption of outgoing data stream and communicates the change to all affected destination and applications​ - Allows working correctly when the CFG frame is not received​ - Parses data without receiving a header frame ... |  | Yes
| Standards | The offered solution allows user defined communication for each incoming data stream separately: - TCP-only - UDP-only - UDP spontaneous (with or without CFG frame) - TCP/UDP method (dual protocol communication) - IPv4 and IPv6 The offered solution will be able to convert data from a transfer protocol to another. |  | Yes
| Standards | The offered solution will provide the capability to send messages to PMU's (e.g; for reconfiguration, parametrization or triggering). The communciation prototocol (TCP, UDP, …) and configuration (CFG) can be defined via the offered solution. |  | No
| Standards | The bidder will explain how CFG (CFG-2, CFG-3) frames will be handles |  | Yes
| Standards | The offered solution will be capable to communicate bi-directionaly in IEC 60870-5-104 protocol in real time |  | Yes
| Standards | The offered solution will be capable to communicate bi-directionaly in TASE.2 (ICCP) protocol in real time |  | No
| Standards | The offered solution will be capable to convert all data from one tranfer protocol to any other protocol indicated above. |  | Yes
| Standards | The Tenderer garantees the solution will support future version of the used applications (database, ...) en operating system (e.g. via updates of the solution) for the total duration of the contract. |  | Yes
| Network | The offered solution will be capable to handle network latency between 1m and 10s and can adjust the wait to it. Latency will not have influenece on any WAMS functionality. |  | Yes
| Network | The offered solution will be redundant over different locations (Elia server rooms in different locations) and be able to handle multicast IEEE C37.118 messages sent by one or more PMU's. |  | Yes
| Network | The offered solution can receive data (from PMU's and PDC's) 2 or more data streams (e.g. for redundancy reasons) |  | Yes
| Network | The offered solution can send data via 2 or more data streams to the same receiver (e.g. for redundancy reasons, different TSO's, ...) |  | Yes
| Network | The offered solution is capable to support synchronisation with server time on which the offered solution is installed on, including NTP (e.g. for latency calculation, PMU data error handling, ...) |  | Yes
| Network | The time alignment of the data streams will be based on the PMU data stream time stamp. |  | Yes
| Network | The offered solution is capable to support PTP for time synchronisation (IEEE1588v2, profile IEC61850-9-3 and profile IEEEC37.238/2017). Exact version and profile can be communicated to the tenderer during tender phase. |  | No
| Network | The offered solution is capable to support GNSS (e.g. GPS, …) for time synchronisation. The Tenderer will indicate which GNSS are supported. |  | No
| Network | Any link of the solution to the internet should be avoided and minimized. In case a an internet connection is required, the Tenderer will clearly indicate which IP addres(ses) and port numbers should be opened. Data components (data storage, data reception, data handling, …) and data processing components will be completely separate from any connection to the internet. All components requiring internet connection will be able to run without internet connection as well, at any moment in time. |  | Yes
| Network | The tendered will indicate what components of the solution require a link to the internet and what's the reason behind. |  | Yes
| Network | The offered solution can be installed fully on premise at Elia premises |  | Yes
| Network | The offered solution should be flexible, scalable, easy updatable against current and feature threats, … The offered solution should favorize approaches that can be fast and easily deployed within Elia’s infrastructure, maintained and updated to reply to above requirements for the total duration of the contract. Solutions requiring substantial installation and/or maintenance resources will be defavorized. |  | No
| Interfaces | The offered solution is capable to provide all received historical and real time PMU data, calculated PMU data, alarming, status, … information to a 3th party application. Real time data can be sent in (very close to) real time to a 3th party application. |  | Yes
| Interfaces | - all this information can be sent via a REST API to a 3th party application. The bidder will indicate what kind of information can not be provided over the API in a performant way (e.g. PMU data) |  | No
| Interfaces | - all this information can be sent via the KAFKA streaming platform to a 3th party application, inclusive raw and calculated PMU data. Real time PMU data, calculated PMU data, alarming, status, ... can be streamed via KAFKA in real time to a 3th party application |  | No
| Interfaces | - If a KAFKA integration is not available yet, the bidder can prove KAFKA integration is on the roadmap and will can be available on the bidders PROD environment within 2 years after contract signature |  | No
| Interfaces | - Other means of communication, streaming, … (e.g. STTP, ...) are available in the offered solution to integrate with a 3th party application. The bidder will indicated what other types of technologies are supported. |  | No
| Interfaces | - all this information can be sent to a data lake. The bidder will indicate which data lakes are supported. |  | No
| Interfaces | - all this information is accessible via database access. The bidder will indicate how secure and no impact on real time operation can be guaranteed. The bidder will indicate which query languages are supported. |  | No
| Interfaces | The offered solution is capable to handle data manipulations via a 3th party application. (getting data from the database, writing data into the database with some adaptations (e.g. calculated data), … The bidder will explain what interface will be provided and what kind of data manipulations will be possible |  | Yes
| Interfaces | The bidder will explain how the interface will be provided. What kind of interface can be communicated in both direction? What mechanisme will be foreseen (e.g. KAFKA interface via subscription on data, RT (or C2RT) data provisiong via KAFKA interface, ...)? |  | Yes
| Interfaces | The offered solution will foresee a python interface to perform data querying and manipulation inside python |  | No
| Interfaces | The offered solution will foresee a matlab interface to perform data querying and manipulation inside matlab |  | No
| Interfaces | The offered solution will provide export functionality into csv,txt files |  | Yes
| Interfaces | The csv,txt export will be configurable. Via the offered solution it will be possible which kind of data can be exported: - a selection (PMU data and/or variables of different PMUs and/or WAMS algorithm result variables) - based on alarms - for a given time interval |  | Yes
| Interfaces | The offered solution will provide manually triggered csv,txt exports. |  | Yes
| Interfaces | The offered solution will provide configuration for (reoccuring) scheduled csv,txt exports. The bidder will explain how (reoccuring) scheduled csv,txt exports are supported |  | No
| Interfaces | The offered solution will provide threshold, trigger and time scheduled based csv,txt exports. The bidder will explain which thresholds/triggers are supported |  | No
| Interfaces | The offered solution will provide export functionality into COMTRADE files |  | No
| Interfaces | The COMTRADE export will be configurable. Via the offered solution it will be possible which kind of data can be exported: - a selection (PMU data and/or variables of different PMUs and/or WAMS algorithm result variables) - based on alarms - for a given time interval |  | No
| Interfaces | The offered solution will provide manually triggered COMTRADE exports. |  | No
| Interfaces | The offered solution will provide configuration for (reoccuring) scheduled COMTRADE exports. The bidder will explain how (reoccuring) scheduled COMTRADE exports are supported |  | No
| Interfaces | The offered solution will provide threshold, trigger and time scheduled based COMTRADE exports. The bidder will explain which thresholds/triggers are supported |  | No
| Interfaces | The offered solution will allow exporting functionalities at specific reporting rates |  | Yes
| Interfaces | If applicable, the bidder will explain any other interfaces. |  | Yes
| Interfaces | The offered solution will be able to pass alarms (or other events) to Microsoft Exchange (e-mail) (On premise version of MS Exchange) for distribution. The solution has the possibility to define different distribution list depeding type of alarms. |  | No
| Interfaces | The offered solution will be able to pass alarms (or other events) to Microsoft Exchange (e-mail) (online (cloud) version of MS Exchange) for distribution. The solution has the possibility to define different distribution list depeding type of alarms. |  | No
| Interfaces | There will be a complete separation between production environment and acceptance/test environment. There will be no common components. |  | Yes
| Database | The offered solution is capable to store all data (PMU data (at the original fps), alarming data, status data, calculated data, …) in a way that allows immediate querying of the contents for data as old as 30 days​. The calculations and the results of the calculations for the storage required will be provided by the tenderer during the offer phase. |  | Yes
| Database | The offered solution is capable to store data older than 30 days for at least 1 year considering 50 fps of synchrophasor data and the relative fps of the results of WAMS analysis including statistical and data quality data. The calculations and the results of the calculations for the storage required will be provided by the tenderer during the offer phase. |  | Yes
| Database | The offered solution is capable to store data older than 30 days for at least 1 year considering 100-200 fps of synchrophasor data and the relative fps of the results of WAMS analysis including statistical and data quality data. The calculations and the results of the calculations for the storage required will be provided by the tenderer during the offer phase. |  | No
| Database | The offered solution is capable to deliver long term storage for triggered data for a period of minimum 5 years. Trigger data is e.g. - automatic triggers based on the value of a variable - boolean values/external variable - Manual trigger (by user) - Selection of data to be stored can be user-definable (e.g. which measurement to store for a given trigger) The calculations and the results of the calculations for the storage required will be provided by the tenderer during the offer phase. |  | Yes
| Database | The offered solution is capable to store the information requested above with the given time interval for at least 250 PMU's and 16 phasors The offered solution is scalable for more PMUs/WAMS results and for storing longer time intervals |  | No
| Database | The offered solution will use database technology designed to handle PMU data, calculated data based on PMU data, … with the corresponding volume requirements, to guarantee good performance for the defined requirements. The tenderer will explain which database technology will be used and how it guarantees good performance in relation to PMU data, calculated data, ... with the corresponding volume requirements. |  | Yes
| Database | The offered solution is easily extendable to handle more data without any major impact on the installation. The Tenderer will explains the limits of the solution. |  | Yes
| Database | The offered solution is capable to store the information requested above with the given time interval for at least 10 lower level PDC's. The offered solution is scalable for more PMUs/WAMS results and for storing longer time intervals |  | No
| Database | The offered solution is capable to prepare an export /query for one hour of measurement of one PMU at maximum orginal fps, minimum 8 phasors in 1 second​. The bidder will guarantee this performance for the contemporary usage of the system by 4 users. It is allowed for older information than 30 days lower performances for information access. The bidder will give indicative values for the given setup described above |  | No
| (Micro) Services | The offered solution is based on a (micro) services architecture. Functionalities like PDC, oscillation monitoring, damping monitoring, … are on itself existing (micro) services inside the architecture of the offered solution |  | No
| (Micro) Services | The (micro) services withing the offered solution can be run on itself and be integrated in an Elia software without the complete offered solution is integrated in the Elia software and without the complete offered solution is operational. |  | No

## Value Definitions
Requirement Category | Minimal Requirement | Answer
Standards | Yes | Yes, standard
Network | No | No, not provided
Interfaces
Database
(Micro) Services