Task 1: Oscillatory Mode Characterization of PMU Measurements

Objective

Develop and implement an automated analytical capability to periodically retrieve historical PMU data and characterize the oscillatory behavior present within the PMU fleet. The capability shall identify and quantify dominant oscillatory modes and associated characteristics, including frequency, amplitude, damping ratio, phase relationships, mode shape, temporal persistence, and confidence. The process shall support efficient analysis of large PMU datasets and provide actionable insights into oscillatory behavior observed across the power system.

Process

1. Automated Data Retrieval and Screening

- Automatically retrieve historical PMU data at configurable intervals (e.g., daily processing of 30-minute data windows).

- Perform data quality checks and preprocessing.

- Identify significant oscillation events and disturbances and optionally exclude those periods from ambient-mode analysis to prevent event-driven oscillations from skewing results. (Real-time oscillation detection and alarming are addressed through a separate online process.)

2. Frequency-Domain Analysis

- Divide the dataset into configurable analysis windows (e.g., 5–10 minutes).

- Perform frequency-domain analysis (FFT, PSD, spectrograms) to identify dominant frequency content and oscillatory energy.

- Track changes in spectral characteristics across analysis windows to assess persistence and temporal variability.

3. Modal Characterization

- Apply modal identification techniques (e.g., Yule-Walker) to estimate:

  - Oscillation frequency

  - Amplitude

  - Damping ratio

  - Growth/decay characteristics

  - Mode confidence

- Identify persistent and poorly damped oscillatory modes that may warrant further engineering investigation.

4. Fleet-Wide Oscillation Assessment

- Evaluate modal observability across PMUs.

- Determine relative amplitude and phase relationships to characterize mode shape and geographic extent.

- Identify PMUs exhibiting the strongest participation in each oscillatory mode.

5. Visualization and Reporting

- Display and export analysis results, including:

  - Dominant frequencies

  - Damping ratios

  - Oscillation amplitudes

  - Phase relationships

  - Mode shapes

  - Temporal trends

  - Confidence metrics

- Generate summary reports and structured output files to support engineering analysis and long-term trend assessment.

Confidence Metric

A confidence metric shall be calculated and reported for each identified oscillatory mode. The confidence metric shall reflect the reliability of the estimate based on factors such as signal-to-noise ratio, persistence across multiple analysis windows, and consistency among analytical methods. This metric shall be used to distinguish meaningful oscillatory modes from noise and spurious detections and to support prioritization of engineering review.