## C37.118 Bandwidth
Courtesy of Schweitzer Engineering Laboratories, Inc. Copyright 2009-2010.
Number of PMUs | 100
For each PMU,
Number of Phasors | 8
Number of Analogs | 0
Number of Digitals | 2
Phasor Format | Floating-point
Freq Format | Floating-point |  |  |  | Integer | Floating-point
Analog Format | Floating-point
Message Rate (msgs /sec) | 30
C37.118 Msg Size (payload only) | 7816 | bytes
Serial Bandwidth Needed | 1875840 | bits/sec | ---> | Note: Bit rate may or may not be equal to the baud rate. Please refer to your serial comm equipment
Total TCP Msg Size | 9136 | bytes | ---> | TCP Overhead calculation: |  |  | for each segment (assuming MSS = 536),
TCP Bandwidth Needed | 2141.25 | Kbits/sec | [5 empty] | TCP header | 20 bytes
UDP Datagram Size | 8896 | bytes |  |  |  | IPv4 header |  | IP header | 20 bytes
UDP Bandwidth Needed | 2085 | Kbits/sec | [5 empty] | Ethernet overhead | 26 bytes | <--- Includes Preamble, SOF, and FCS
[8 empty] | Ethernet inter-frame gap | 22 bytes
[8 empty] | Total | 88 bytes
Note: The overhead calculation is just an estimate. It can vary depending on the IP options, fragmentation, re-transmissions, etc.

## GEP Bandwidth
Gateway Protocol Bandwidth Estimator
Field | Bytes
Flags | 1
ID | 2
Value | 4
Time | 8 | max value
Total: | 15
Avg. points / PMU: |  | 10
Total Bytes / PMU: |  | 150
Frame per second: |  | 30
Number of PMU's: |  | 50
Uncompressed bps: |  | 225000
Avg. Compression: |  | 65%
Compressed bps: |  | 78750
UDP Overhead: |  | 89334
Bandwidth Needed: |  | 697.9219 | Kbps
http://www.gridprotectionalliance.org/technology.asp#gep

## Binary Storage Calculation
Courtesy of Schweitzer Engineering Laboratories, Inc. Copyright 2009-2010.
Phasor Format | Floating-point |  | Floating-point
Analog Format | Floating-point |  | Integer
Freq Format | Floating-point
Fields | Count | Field Size (bytes)
Status | 0 | 0
Frequency | 1 | 4
Df/Dt | 1 | 4
Phasors | 3 | 24
Analogs | 2 | 8
Digital Words | 0 | 0
Number of PMUs | 20
Overhead per sample | 40 | bytes
Message rate | 50 | messages per second
PMU data size | 40 | bytes
Sample Size | 840 | bytes
I/O Writes | 41.0156 | KB per second
Size | 42000 | bytes per second
| 2520000 | bytes per minute
| 144.1956 | MB per hour
| 3460.6934 | MB per day
| 101.3875 | GB per month
| 1233.5479 | GB per year